## Total Address Range
Size of global address fields
%M | 32634
%MW | 32634
Estop | %M1 |  |  | %MW1 | iPad1_PumpNumber
PlayList Mode | %M2 |  | %MW2 | %MW20 | Pump Details 1
Play_status | %M3 |  |  | %MW21 | iPad2_PumpNumber
Deadman Switch Enable | %M4 |  | %MW22 | %MW40 | Pump Details 2
|  |  |  | %MW49 | Set All Animated Pumps to Auto
Show Stoppers | %M5 | %M20
System Status | %M21 | %M199 | %MW60 | %MW70 | Panel Light Status
Ethernet Status | %M200 | %M299 | %MW100 | %MW110 | Time Sync
Water Quality | %M300 | %M649 | %MW300 | %MW649 | Water Quality
Temperature | %M650 | %M799 | %MW650 | %MW799 | Temperature
Wind Spd & Dir | %M800 | %M850 | %MW800 | %MW850 | Wind Spd & Dir | Pumps
Fire | %M851 | %M999 | %MW851 | %MW999 | Fire | Pumps with VFDs | 1000 | 1999
Pumps | %M1000 | %M2999 | %MW1000 | %MW2999 | Pumps | Pump Schedule | 2000 | 2249
Water Level | %M3000 | %M3499 |  |  | Water Level | Motor Starters | 2250 | 2999
Lights | %M3500 | %M3999 |  |  | Lights
Air Pressure Sensor | %M4000 | %M4499 | %MW4000 |  | Air Pressure Sensors | Warning_Status | %M10501
Strainer | %M4500 | %M4999 |  |  | Strainer | Fault_Status | %M10502
| %M5000 | %M5499 |  |  | System Alarms | Warning_Reset | %M10503
| %M5500 | %M5999 |  |  | Show Stoppers | Fault_Reset | %M10504
BenderStatus | %M6000 | %M6499 |  |  | Eq2 Sch
Timers | %M6500 | %M6999 | %MW6500 | %MW6999 | Timer
Fog | %M7000 | %M8000 |  |  | Fog
Misc | %M8000 | %M9999 |  |  | Misc
| iPad1_PumpNumber | %MW1 | %MW21 | iPad2_PumpNumber
| Manual_Speed | %MW2 | %MW22 | Manual_Speed
| Output_Freq | %MW3 | %MW23 | Output_Freq
| Current | %MW4 | %MW24 | Current
| Voltage | %MW5 | %MW25 | Voltage
| Temperature | %MW6 | %MW26 | Temperature
| Auto_Mode | %MW7 | %MW27 | Auto_Mode
| Manual_Mode | %MW8 | %MW28 | Manual_Mode
| Manual_Start | %MW9 | %MW29 | Manual_Start
| Mode_Feedback | %MW10 | %MW30 | Mode_Feedback
| Man_Speed2 | %MW11 | %MW31 | Man_Speed2
| Pump Fault | %MW12.0 | %MW32.0 | Pump Fault
| Press Fault | %MW12.1 | %MW32.1 | Press Fault
| VFD Fault | %MW12.2 | %MW32.2 | VFD Fault
| GFCI Fault | %MW12.3 | %MW32.3 | GFCI Fault
| Network Fault | %MW12.4 | %MW32.4 | Network Fault
| Mode_Feedback | %MW12.5 | %MW32.5 | Mode_Feedback
| CleanStrainer_Warning | %MW12.6 | %MW32.6 | CleanStrainer_Warning
| Run_status | %MW12.7 | %MW32.7 | Run_Status
| Low_WaterLevel | %MW12.8 | %MW32.8 | Low_WaterLevel
| Hz Max | %MW13 | %MW33 | Hz Max
| Voltage Max | %MW14 | %MW34 | Voltage Max
| Voltage Min | %MW15 | %MW35 | Voltage Min
| Current Max | %MW16 | %MW36 | Current Max
| Temp Max | %MW17 | %MW37 | Temp Max
| unassigned | %MW18 | %MW38 | unassigned
| unassigned | %MW19 | %MW39 | unassigned
| unassigned | %MW20 | %MW40 | unassigned
| Set All Pumps Auto | %MW49

## PLC IOs
m340 @ CP-101
Digital Inputs |  |  | Digital Outputs
In_System_Warning_reset | %I0.2.0 | EBOOL | Out_System_Normal | %Q0.7.0 | EBOOL
In_System_Fault_reset | %I0.2.1 | EBOOL | Out_System_Warning | %Q0.7.1 | EBOOL
In_ACP101_Estop | %I0.2.2 | EBOOL | Out_System_Fault | %Q0.7.2 | EBOOL
In_MCC101_Estop | %I0.2.3 | EBOOL | Out_ACP101_Estop_Status | %Q0.7.3 | EBOOL
In_MCC101_Estop | %I0.2.4 | EBOOL | Out_MCC101_Estop_Status | %Q0.7.4 | EBOOL
In_MCC102_Estop | %I0.2.5 | EBOOL | Out_MCC102_Estop_Status | %Q0.7.5 | EBOOL
| %I0.2.6 | EBOOL | Out_LCP101_Estop_Status | %Q0.7.6 | EBOOL
In_FS101_Overflow | %I0.2.7 | EBOOL | Out_Ozone_Generator | %Q0.7.7 | EBOOL
In_F100_PSL1000_CleanStrainer | %I0.2.8 | EBOOL |  | %Q0.7.8 | EBOOL
In_F101_PSL1001_CleanStrainer | %I0.2.9 | EBOOL |  | %Q0.7.9 | EBOOL
In_PSL1002_Call4BW | %I0.2.10 | EBOOL |  | %Q0.7.10 | EBOOL
In_F103_PSL1003_CleanStrainer | %I0.2.11 | EBOOL |  | %Q0.7.11 | EBOOL
In_PSDSH1000_Call4BW | %I0.2.12 | EBOOL |  | %Q0.7.12 | EBOOL
In_P100A_PSLL_Ok (NC??) | %I0.2.13 | EBOOL |  | %Q0.7.13 | EBOOL
In_P101_PSLL_Ok | %I0.2.14 | EBOOL |  | %Q0.7.14 | EBOOL
In_Enable_Bromine_FSL1000 | %I0.2.15 | EBOOL |  | %Q0.7.15 | EBOOL
In_LSHH1001_HighWaterAlarm | %I0.3.0 | EBOOL | Out_WaterMakeup_LV1001 | %Q0.8.0 | EBOOL
In_LSH1001_MakeupOff | %I0.3.1 | EBOOL | Out_Brominator_KV1001 | %Q0.8.1 | EBOOL
In_LSK1001_MakeupOn | %I0.3.2 | EBOOL | Out_BW1_Valve | %Q0.8.2 | EBOOL
in_LSLL1001_LightsOff | %I0.3.3 | EBOOL | Out_BW2_Valve | %Q0.8.3 | EBOOL
In_P102_PSLL_Ok | %I0.3.4 | EBOOL | Out_BMS1 | %Q0.8.4 | EBOOL
In_P103_PSLL_Ok | %I0.3.5 | EBOOL | Out_BMS2 | %Q0.8.5 | EBOOL
In_P104_PSLL_Ok | %I0.3.6 | EBOOL | Out_DrainValve_1 | %Q0.8.6 | EBOOL
In_P105_PSLL_Ok | %I0.3.7 | EBOOL | Out_DrainValve_2 | %Q0.8.7 | EBOOL
In_P106_PSLL_Ok | %I0.3.8 | EBOOL | Out_DrainValve_3 | %Q0.8.8 | EBOOL
In_P107_PSLL_Ok | %I0.3.9 | EBOOL | Out_DrainValve_4 | %Q0.8.9 | EBOOL
In_P108_PSLL_Ok | %I0.3.10 | EBOOL | Out_DrainValve_5 | %Q0.8.10 | EBOOL
In_P109_PSLL_Ok | %I0.3.11 | EBOOL | Out_DrainValve_6 | %Q0.8.11 | EBOOL
In_P110_PSLL_Ok | %I0.3.12 | EBOOL | Out_DrainValve_7 | %Q0.8.12 | EBOOL
In_P111_PSLL_Ok | %I0.3.13 | EBOOL | Out_MS101B_ON | %Q0.8.13 | EBOOL
In_P112_PSLL_Ok | %I0.3.14 | EBOOL | Out_MS131_ON | %Q0.8.14 | EBOOL
In_P113_PSLL_Ok | %I0.3.15 | EBOOL | Out_MS132_ON | %Q0.8.15 | EBOOL
In_P114_PSLL_Ok | %I0.4.0 | EBOOL
In_LSH2001_MakeupOff | %I0.4.1 | EBOOL
In_LSL2001_MakeupOn | %I0.4.2 | EBOOL
In_LSLL2001_LowWaterAlarm | %I0.4.3 | EBOOL
In_LSL1002_LightsOff | %I0.4.4 | EBOOL
In_LSL1003_LightsOff | %I0.4.5 | EBOOL
In_LSL1004_LightsOff | %I0.4.6 | EBOOL
| %I0.4.7 | EBOOL
In_LSH1005 | %I0.4.8 | EBOOL
In_LSH1006 | %I0.4.9 | EBOOL
In_LSH1007 | %I0.4.10 | EBOOL
In_LSH1008 | %I0.4.11 | EBOOL
In_LSH1009 | %I0.4.12 | EBOOL
In_LSH1010 | %I0.4.13 | EBOOL
In_LSH1011 | %I0.4.14 | EBOOL
In_LSH1012 | %I0.4.15 | EBOOL
In_LSH1013 | %I0.5.0 | EBOOL | Analog Inputs
In_LSH1014 | %I0.5.1 | EBOOL | In_pH | %CH0.9.0 | T_ANA_IN_BMX
In_LSH1015 | %I0.5.2 | EBOOL | In_ORP | %CH0.9.1 | T_ANA_IN_BMX
In_LSH1016 | %I0.5.3 | EBOOL | In_TDS | %CH0.9.2 | T_ANA_IN_BMX
| %I0.5.4 | EBOOL |  | %CH0.9.3 | T_ANA_IN_BMX
| %I0.5.5 | EBOOL |  | %CH0.9.4 | T_ANA_IN_BMX
| %I0.5.6 | EBOOL |  | %CH0.9.5 | T_ANA_IN_BMX
| %I0.5.7 | EBOOL |  | %CH0.9.6 | T_ANA_IN_BMX
In_MS101B_OnStatus | %I0.5.8 | EBOOL |  | %CH0.9.7 | T_ANA_IN_BMX
In_MS101B_Overload | %I0.5.9 | EBOOL
In_MS131_OnStatus | %I0.5.10 | EBOOL
In_MS131_Overload | %I0.5.11 | EBOOL
In_MS132_OnStatus | %I0.5.12 | EBOOL
In_MS132_Overload | %I0.5.13 | EBOOL
| %I0.5.14 | EBOOL
| %I0.5.15 | EBOOL
| %I0.6.0 | EBOOL
| %I0.6.1 | EBOOL
| %I0.6.2 | EBOOL
| %I0.6.3 | EBOOL
| %I0.6.4 | EBOOL
| %I0.6.5 | EBOOL
| %I0.6.6 | EBOOL
| %I0.6.7 | EBOOL
| %I0.6.8 | EBOOL
| %I0.6.9 | EBOOL
| %I0.6.10 | EBOOL
| %I0.6.11 | EBOOL
| %I0.6.12 | EBOOL
| %I0.6.13 | EBOOL
| %I0.6.14 | EBOOL
| %I0.6.15 | EBOOL

## System Status
Server Path
Server Path | readplayStatus
Sample Response | [
{
"Play Mode": 0,
"play status": 0,
"Current Show": 0,
"deflate": "nothing",
"next Show Time": 0,
"next Show Num": 0
}
]
Server Path | readStatusLog
Sample Response | [
{
"EStop": [
1,
0,
0,
0,
0,
0,
0,
0,
0,
0,
0,
0,
0,
0
],
"PlayMode": 0,
"playStatus": 0,
"CurrentShow": 0,
"deflate": "nothing",
"nextShowTime": 0,
"nextShowNumber": 0,
"timeLastCmnd": 0,
"spm_RAT_Mode": false,
"dayMode": 0,
"ShowStoppers": [
0,
0,
0,
0,
0,
0,
0,
0,
0,
0,
0,
0,
0,
0,
0,
0
],
"Temp": [
0
],
"Wind_Sensors": [
1,
1,
0,
1,
1,
1,
0,
0
],
"PumpFaults": [
1,
1,
1,
1,
1,
1,
1,
1,
1,
1,
1,
1,
1,
1,
1,
1
],
"WaterLevel": [
0,
1,
0,
0,
1
],
"WaterFilter": [
1,
1,
1
],
"statusLights": [
1
],
"Filtration": [
1,
1,
1
],
"WaterQuality": [
1,
0,
0,
1,
0,
0,
0,
0
],
"BMS_Status": [],
"JumpToStepAuto": 0,
"JumpToStepManual": 0,
"SPM_Heartbeat": 53,
"SPM_Modbus_Connection": false,
"PLC_Heartbeat": 0,
"PLC_Modbus _Connection": true
}
]

## Panel Lights
YELLOW |  |  | RED
System Warning LED | %MW60 | INT | System Fault LED | %MW65 | INT
Clean Strainer | Bit 0 | BOOL | WaterWall Pump Fault | Bit 0 | BOOL
Br Timeout | Bit 1 | BOOL | Filter Pump Fault | Bit 1 | BOOL
Water Makeup Timeout | Bit 2 | BOOL | Animated Pump Fault | Bit 2 | BOOL
WQ Warning | Bit 3 | BOOL | Water level Fault | Bit 3 | BOOL
unassigned | Bit 4 | BOOL | Water Quality Fault | Bit 4 | BOOL
unassigned | Bit 5 | BOOL | Estop | Bit 5 | BOOL
unassigned | Bit 6 | BOOL | Fog Pump Fault | Bit 6 | BOOL
unassigned | Bit 7 | BOOL | Network Fault | Bit 7 | BOOL
unassigned | Bit 8 | BOOL | unassigned | Bit 8 | BOOL
unassigned | Bit 9 | BOOL | unassigned | Bit 9 | BOOL
unassigned | Bit 10 | BOOL | unassigned | Bit 10 | BOOL
unassigned | Bit 11 | BOOL | unassigned | Bit 11 | BOOL
unassigned | Bit 12 | BOOL | unassigned | Bit 12 | BOOL
unassigned | Bit 13 | BOOL | unassigned | Bit 13 | BOOL
unassigned | Bit 14 | BOOL | unassigned | Bit 14 | BOOL
unassigned | Bit 15 | BOOL | unassigned | Bit 15 | BOOL

## Ethernet
0 - bad , 1 - good
Ethernet_Status_1 | %M121 | EBOOL |  | VFD-100A | FilterPump
Ethernet_Status_2 | %M122 | EBOOL |  | VFD-101 | Animated
Ethernet_Status_3 | %M123 | EBOOL |  | VFD-102
Ethernet_Status_4 | %M124 | EBOOL |  | VFD-103
Ethernet_Status_5 | %M125 | EBOOL |  | VFD-104
Ethernet_Status_6 | %M126 | EBOOL |  | VFD-105
Ethernet_Status_7 | %M127 | EBOOL |  | VFD-106
Ethernet_Status_8 | %M128 | EBOOL |  | VFD-107
Ethernet_Status_9 | %M129 | EBOOL |  | VFD-108
Ethernet_Status_10 | %M130 | EBOOL |  | VFD_111 | Central Cascade Pump
Ethernet_Status_11 | %M131 | EBOOL |  | VFD_112 | Reflecting Pool Pump
Ethernet_Status_12 | %M132 | EBOOL |  | VFD_200 | FilterPump
Ethernet_Status_13 | %M133 | EBOOL |  | VFD_109 | Animated
Ethernet_Status_14 | %M134 | EBOOL |  | VFD_110
Ethernet_Status_15 | %M135 | EBOOL |  | VFD_113
Ethernet_Status_16 | %M136 | EBOOL |  | VFD_114

## Pumps
Filtration | 3xx Series Vortex Pumps
1001 |  | P101_Auto_Mode | %M1001 | EBOOL | fixed | 0 | 1 |  | iPad Number | 106
101 |  | P101_Man_Mode | %M1002 | EBOOL | fixed | 1 | 2 |  | Starting Address | 1071
|  | P101_Man_Start | %M1003 | EBOOL | fixed | 1 | 3
|  | VFD_Run Status | %M1004 | EBOOL |  |  | 4
|  | Pump At Target Freq | %M1005 | EBOOL |  |  | 5 | PLC Addr # | Device Name | Device Description | Address |  | iPad Pump Number
|  | VFD Fault | %M1006 | EBOOL |  |  | 6 |  |  |  | Modbus | IP Address |  | Panel | Amp | Voltage | Hz
|  | Pressure Fault | %M1007 | EBOOL |  |  | 7 | 1 | VFD-100A | FilterPump |  |  | 1001 | MCC-101 | 14 | 480Y/277AC | 60 | manual only | schedule
|  | Pump Fault | %M1008 | EBOOL |  |  | 8 | 2 | VFD-101 | Surge Pump 5hp |  |  | 101 |  | 7.5 |  |  | autohand
|  | VFD Warning | %M1009 | EBOOL |  |  | 9 | 3 | VFD-102 | Surge Pump 5hp |  |  | 102 |  | 7.5 |  |  | autohand
|  | Modbus TCP Active | %M1010 | EBOOL |  |  | 10 | 4 | VFD-103 | Surge Pump 5hp |  |  | 103 |  | 7.5 |  |  | autohand
|  | VFD on HMI | %M1011 | EBOOL |  |  | 11 | 5 | VFD-104 | Surge Pump 5hp |  |  | 104 |  | 7.5 |  |  | autohand
|  | Backwash Running | %M1012 | EBOOL |  |  | 12 | 6 | VFD-105 | Surge Pump 5hp |  |  | 105 |  | 7.5 |  |  | autohand
|  | Strainer Warning | %M1013 | EBOOL |  |  | 13 | 7 | VFD-106 | Surge Pump 5hp |  |  | 106 |  | 7.5 |  |  | autohand
|  | Network Connection | %M1014 | EBOOL |  |  | 14 | 8 | VFD-107 | Runnel Pump 3hp |  |  | 107 |  | 4.8 |  |  | manual only
|  | Manual Speed | %MW1001 | INT |  |  | 1 | 9 | VFD-108 | Runnel Pump 3hp |  |  | 108 |  | 4.8 |  |  | manual only
|  | Output Freq | %MW1002 | INT |  |  | 2 | 10 | VFD_111 | Central Cascade Pump 20hp |  |  | 111 | MCC-102 | 27 |  |  | autohand
|  | P102_Current | %MW1003 | INT |  |  | 3 | 11 | VFD_112 | Reflecting Pool Pump |  |  | 112 |  | 34 |  |  | autoHand
|  | Voltage | %MW1004 | INT |  |  | 4 | 12 | VFD_200 | FilterPump 3hp |  |  | 200 |  | 4.8 |  |  | manual only | schedule
|  | Temperature | %MW1005 | INT |  |  | 5 | 13 | VFD_109 | West Fill Pump 7.5hp |  |  | 109 |  | 11 |  |  | PLC
|  | VFD Fault Code | %MW1006 | INT |  |  | 6 | 14 | VFD_110 | East Fill Pump 7.5hp |  |  | 110 |  | 11 |  |  | PLC
|  | BW Speed | %MW1007 | INT |  |  | 7 | 15 | VFD_113 | Canyon Lake 3 hp |  |  | 113 |  | 4.8 |  |  | manual only
[7 empty] | 8 | 16 | VFD_114 | Apache Lake 3hp |  |  | 114 |  | 4.8 |  |  | manual only
9
All Other Pumps | [7 empty] | 2251 |  | P102_Pump_Start | %M2251 | EBOOL | Filtration Pump Run Status
1071 |  | P101_Auto_Mode | %M1071 | EBOOL |  |  |  | P-100B - Ozonator (runs when Filtration Pump is running) |  | P102_Pump_Running | %M2252 | EBOOL
101 |  | P101_Man_Mode | %M1072 | EBOOL | [5 empty] | P102_Pump_Fault | %M2253 | EBOOL
|  | P101_Man_Start | %M1073 | EBOOL | [5 empty] | P102_Pump_Overload | %M2254 | EBOOL
|  | VFD_Run Status | %M1074 | EBOOL | [5 empty] | P102_Pressure_Fault | %M2255 | EBOOL
|  | Pump At Target Freq | %M1075 | EBOOL
|  | VFD Fault | %M1076 | EBOOL | [5 empty] | Air Suction
|  | Pressure Fault | %M1077 | EBOOL |  |  |  | 2256 |  | P213_Pump_Start | %M2256 | EBOOL
|  | Pump Fault | %M1078 | EBOOL |  |  |  | P-131 - West Vacuum Blower Pump |  | P213_Pump_Running | %M2257 | EBOOL
|  | VFD Warning | %M1079 | EBOOL | [5 empty] | P213_Pump_Fault | %M2258 | EBOOL
|  | Modbus TCP Active | %M1080 | EBOOL | [5 empty] | P213_Pump_Overload | %M2259 | EBOOL
|  | VFD on HMI | %M1081 | EBOOL | [5 empty] | P213_Pressure_Fault | %M2260 | EBOOL
|  | Backwash Running | %M1082 | EBOOL | [5 empty] | Air Suction
|  | unused | %M1083 | EBOOL |  |  |  | 2261 |  | P413_Pump_Start | %M2261 | EBOOL |  |  |  |  | READ ONLY
|  | Network Connection | %M1084 | EBOOL |  |  |  | P-132 - East Vacuum Blower Pump |  | P413_Pump_Running | %M2262 | EBOOL |  |  |  |  | PLC - INTERNAL - iPad Settings Screen
|  | Manual Speed | %MW1071 | INT | [5 empty] | P413_Pump_Fault | %M2263 | EBOOL |  |  |  |  | WRITE - USER SETTINGS
|  | Output Freq | %MW1072 | INT | [5 empty] | P413_Pump_Overload | %M2264 | EBOOL
|  | P102_Current | %MW1073 | INT | [5 empty] | P413_Pressure_Fault | %M2265 | EBOOL
|  | Voltage | %MW1074 | INT
|  | Temperature | %MW1075 | INT
|  | VFD Fault Code | %MW1076 | INT
|  | BW Speed | %MW1077 | INT
0 - Active , 1 - Disabled
[8 empty] | WaterWall Filler Show Schedule |  | WW_FillerShow_mode | %M2000 | EBOOL |  |  |  | Auto mode - Schedule is active, manual mode - lets user ramp pump up and down individually
[10 empty] | WW_FillerShow_Sch_ON | %M2001 | EBOOL |  |  |  | Server only
[10 empty] | FillerShow_manualON | %M2002 | EBOOL
[10 empty] | FillerShow_Status | %M2003 | EBOOL
[10 empty] | FillerShow_PumpSpeed | %MW2000 | INT | 0-500 | (Hz * 10)
[9 empty] | ServerPath | readFillerShowSch
writeFillerShowSch
[9 empty] | Sample Response | [ 1, 1800, 2259, 0, 1800, 2258, 0, 1800, 2258, 0, 1800, 2258, 0, 1800, 2258, 1, 1800, 2259, 1, 1800, 2259 ]
[9 empty] | Comments | 1: Weekend, 0 - WeekDay
[8 empty] | Filtration Schedule |  | FiltrationPump_mode | %M2010 | EBOOL
[10 empty] | Filtration_Schedule_ON | %M2011 | EBOOL |  |  |  | Server only
[10 empty] | Filtration1_ON | %M2012 | EBOOL
[10 empty] | Filtration1_Status | %M2013 | EBOOL
[9 empty] | ServerPath | readFilterSch
writeFilterSch
[9 empty] | Sample Response | [ 1, 1800, 2259, 0, 1800, 2258, 0, 1800, 2258, 0, 1800, 2258, 0, 1800, 2258, 1, 1800, 2259, 1, 1800, 2259 ]
[9 empty] | Comments | 1: Weekend, 0 - WeekDay

## Strainer
Strainer |  |  |  | Name
| Clean_Strainer1 | %M4500 | EBOOL | In_F101_PSL1001_CleanStrainer
| Clean_Strainer2 | %M4501 | EBOOL | In_F103_PSL1002_CleanStrainer
| Clean_Strainer3 | %M4502 | EBOOL | In_F104_PSL2001_CleanStrainer

## Water Level
Water Level Sensors |  | 7 in total | Water Makeup only for LT 110
3000 |  | WL_Above_H | %M3000 | EBOOL | Client - READ ONLY
T1 | LS1001 | WL_Below_L | %M3001 | EBOOL | Client - WRITE -
|  | WL_Below_LLA | %M3002 | EBOOL | Settings Screen - write
|  | WL_Below_LLB | %M3003 | EBOOL | Settings Screen - read only
|  | WL_Below_LLL | %M3004 | EBOOL | PLC (Internal)
|  | WL_Malfunction | %M3005 | EBOOL
|  | WL_WaterMakeup | %M3006 | EBOOL
|  | WL_WMakeup_Timeout | %M3007 | EBOOL

## Lights
Lights
3500 |  | Lights_Auto_Man_mode | %M3500 | EBOOL
Lights |  | Light_Schedule_ON | %M3501 | EBOOL | Server only | READ ONLY
|  | LCP101_ON | %M3502 | EBOOL |  | PLC - INTERNAL - iPad Settings Screen
|  | LCP101_Status | %M3503 | EBOOL |  | WRITE - USER SETTINGS
PLC (Internal)
| ServerPath | readLights
writeLights
| Sample Response | [ 1, 1800, 2259, 0, 1800, 2258, 0, 1800, 2258, 0, 1800, 2258, 0, 1800, 2258, 1, 1800, 2259, 1, 1800, 2259 ]
| Comments | 1: Weekend, 0 - WeekDay
| ServerPath | setDayMode
| Sample Query | 0 or 1
| Comments | 0 = Lights ON, 1 = lights OFF
read response from /readSystemStatus

## Timer
| Address | TYPE | Default | Range |  | Units
T_Pumps_Pressure_Switch | %MW6500 | INT | 10 | 0 | 60 | sec
T_pH | %MW6501 | INT | 10 | 0 | 60 | sec
T_ORP | %MW6502 | INT | 10 | 0 | 60 | sec | READ ONLY
T_TDS | %MW6503 | INT | 10 | 0 | 60 | sec | Settings Screen - write
T_Water_Temp | %MW6504 | INT | 10 | 0 | 60 | sec | WRITE - USER SETTINGS
T_Air_Temp | %MW6505 | INT | 10 | 0 | 60 | sec | PLC (Internal)
T_Dump_Valve | %MW6506 | INT | 5 | 0 | 60 | mins
T_Wind_Bits_ON | %MW6507 | INT | 15 | 0 | 60 | sec
T_Wind_Bits_OFF | %MW6508 | INT | 15 | 0 | 60 | sec
T_Wind_Abort | %MW6509 | INT | 15 | 0 | 60 | sec
T_Water_Above_H | %MW6510 | INT | 5 | 0 | 5 | sec
T_Water_Below_L | %MW6511 | INT | 10 | 0 | 30 | sec
T_Water_Below_LL | %MW6512 | INT | 10 | 0 | 30 | sec
T_Water_Below_LLL | %MW6513 | INT | 10 | 0 | 30 | sec
T_BW_Duration | %MW6514 | INT | 15 | 0 | 30 | sec
T_PDSH_Delay | %MW6515 | INT | 3 | 0 | 10 | mins
T_BWValve_Activation | %MW6516 | INT | 0 | 0 | 24 | h
T_Strainer_Pressure_Switch | %MW6517 | INT | 10 | 0 | 60 | sec
T_WaterMakeup | %MW6518 | INT | 3 | 0 | 24 | h
T_Brominator | %MW6519 | INT | 8 | 0 | 24 | h
T_Fog_MS_Delay | %MW6520 | INT | 5 | 0 | 30 | sec
T_Fog_Water_level_Timeout | %MW6521 | INT | 60 | 0 | 600 | min
T_WindAbort_Unlatch | %MW6522 | INT | 1 | 0 | 5 | min
T_Fog_Booster_TimeOff | %MW6523 | INT | 15 | 0 | 30 | sec
| %MW6524 | INT
| %MW6525 | INT

## Backwash
Filtration Skid
BW Routine
BW | Duration_SP | %MW6514 | INT
| BW_ValveActuation_Time | %MW6516 | INT
| Trigger_Sch_BW | %M4000 | EBOOL
| BW1_Running | %M4001 | EBOOL
| iPad_BW1_Trigger | %M4002 | EBOOL
| BW2_Running | %M4003 | EBOOL
| iPad_BW2_Trigger | %M4004 | EBOOL
ServerPath | readBW | Comments
Sample Response | {
| "BWshowNumber": 999, | Show Manual BW button only if ManBWcanRun == 1
"duration": 1,
| "SchBWStatus": 0, | display "blockBWuntil"
"timeout": 86400,
"timeoutCountdown": 0,
"timeLastBW": 0,
"trigBacklog": 1,
"manBWcanRun": 1,
"PDSH_req4BW": 0,
"schDay": 2,
"schTime": 1545,
"blockBWuntil": 0
}
ServerPath | writeBW | Comments
Sample query | [schDay,schTime] | schday: 1-7
schTime: 0-2359

## Water Quality
300 | pH | pH_Scaled_Value | %MW300 | REAL
|  | pH_Scale_Min | %MW302 | REAL |  | Client - READ ONLY
|  | pH_Scale_Max | %MW304 | REAL |  | Client - WRITE -
|  | pH_Lo_SP | %MW306 | REAL |  | Settings Screen - write
|  | pH_Hi_SP | %MW308 | REAL |  | Settings Screen - read only
|  | pH_Channel_Fault | %M300 | EBOOL |  | PLC (Internal)
|  | pH_Above_Hi | %M302 | EBOOL
|  | pH_Below_Low | %M304 | EBOOL
| ORP | ORP_Scaled_Value | %MW310 | REAL
|  | ORP_Scale_Min | %MW312 | REAL
|  | ORP_Scale_Max | %MW314 | REAL
|  | ORP_Lo_SP | %MW316 | REAL | for alarm
|  | ORP_Hi_SP | %MW318 | REAL | for alarm
|  | ORP_Channel_Fault | %M310 | EBOOL
|  | ORP_Above_Hi | %M312 | EBOOL
|  | ORP_Below_Low | %M314 | EBOOL
| TDS | TDS_Scaled_Value | %MW320 | REAL
|  | TDS_Scale_Min | %MW322 | REAL
|  | TDS_Scale_Max | %MW324 | REAL
|  | TDS_Lo_SP | %MW326 | REAL
|  | TDS_Hi_SP | %MW328 | REAL
|  | TDS_Channel_Fault | %M320 | EBOOL
|  | TDS_Above_Hi | %M322 | EBOOL
|  | TDS_Below_Low | %M324 | EBOOL
| Br Dosing | Br_Enabled | %M325 | EBOOl
|  | Br_Dosing | %M326 | EBOOL
|  | Br_Timeout | %M327 | EBOOL
|  | Br_Dosing_ON_SP | %MW330 | REAL | for dosing
|  | Br_Dosing_OFF_SP | %MW332 | REAL | for dosing
| ServerPath | WQ_Live
| Sample Response | {"orp" : [], "ph" : [], "tds" :[], "br" : [], "date" : []}
| Comments | 900 elements, 1 each second
contains last 15mins of info
| ServerPath | WQ_Day
| Sample Response | {"orp" : [], "ph" : [], "tds" :[], "br" : [], "date" : []}
| Comments | upto 1440 elements, 1 each min
contains last 24hr of info
| ServerPath | WQ_Week
| Query | 0 to 6
| Sample Response | {"orp" : [], "ph" : [], "tds" :[], "br" : [], "date" : []}
| Comments | query is day value. Server checks and ignores current day value
Contains only that particular day's data
upto 1440 elements, 1 each min.

## TimeSync
Server handles the times. Not the PLC
ServerPath | /readServerTime
Sample Response | YYYY-MM-DD-HH-MM-SS
Comments | directly display text on the settings screen
Time_dayOfWeek | %MW100 | INT | read by Server
Time_Seconds | %MW101 | INT
Time_Hour | %MW102 | INT
Time_Month | %MW103 | INT
Time_Century | %MW104 | INT
Time_iPad_Seconds | %MW106 | INT | set by iPad
Time_iPad_Hour | %MW107 | INT
Time_iPad_Month | %MW108 | INT
Time_iPad_Century | %MW109 | INT
Time_iPad_Set | %MW110 | INT | pulse ON/OFF

## Misc Server Paths
ServerPath
Sample Response
Comments